## Slide 1: The Basics of Solar
By Antony Cartwright

## Slide 2: Main Points
Solar Panels
On/Off Grid
Charge Controllers
Battery Banks
Inverters
Wiring
Fuses & Safety
Efficiency
Calculating Need

## Slide 3: Solar Panel Types
Two Main Types:
Monocrystalline – Expensive but slightly better.
Polycrystalline – Cheaper but not quite as good.

## Slide 4: Solar Panel Sizing
Physical dimensions
Watts (Volts & Amperage)
Voltages can vary (typically 12v/24v)

## Slide 5: Solar Panel Wiring
Solar panels can be wired either in parallel or series.
Series increases potential difference (voltage), amperage stays the same.
Parallel increases amperage, voltage stays the same.

## Slide 6: Solar Panel Irradiation
Irradiation is exposure to the suns rays. We want maximum exposure.
The tilt of a panel matters! The sun has a different elevation at different times of the year. It’s higher up in the summer, lower in the winter.
The direction of a panel matters! The sun rises in the east and sets in the west.

## Slide 7: Solar Panel Irradiation (Cont)
The average amount of sunlight. There are no hard and fast figures, but research generally shows that there are 2hrs per day in winter and 6hrs a day in summer.
How to calculate what your panels can generate. Roughly Watts x Hours.
For example; 200W panel x 2hrs of good sunlight = 400WH.

## Slide 8: On Grid Vs Off Grid
On Grid:
Energy produced is not stored.
It’s sent to the grid.
Cheaper on equipment costs.
You still rely on the grid to buy back energy.
Off Grid:
Energy is stored.
It’s not send to the grid.
More expensive on equipment costs.
You “do not” have to rely on the grid to supply energy.

## Slide 9: Charge Controllers
A charge controller controls the charging of your batteries.
Prevents over-charge.
Helps to lengthen the lifespan of your battery bank.

## Slide 10: Charge Controllers (Cont)
Two types:
PWM:
Designed to work with one set voltage – all equipment must be the same voltage rating.
Generally not as efficient.
A lot Cheaper.
MPPT:
Can work with multiple voltages - gives flexibility.
Generally very efficient.
Considerably more expensive.

## Slide 11: Charge Controllers (Cont)
If MPPT, choose a reputable brand as there are fakes.
Charge controllers are sold by amperage rating.
Overly high amperage requires thicker components and therefore more expensive.
Overly low amperage will overheat and damage the unit.

## Slide 12: Battery Banks
Battery banks store your energy.
Battery banks need a bank voltage, usually 12v, 24v, 36v or 48v.
Higher voltage banks do not need to deliver as much current (comparatively).
Higher voltage (and less current) means thinner cables – Cheaper.
Higher voltage means less power loss over distance. Saves energy.

## Slide 13: Battery Banks (Cont)
A battery bank may consist of one or more groups of batteries.
Each battery has 2 important ratings: Voltage and AH.
Voltage is the ‘pressure’ of which it can deliver current.
AH is the amount of current it can store.
Batteries can be wired up in series to increase voltage, or parallel to increase capacity.

## Slide 14: Battery Banks (Cont)
Main type of battery for solar is lead acid.
Lead acid shouldn’t be 100% discharged.
The more discharged it is, for the greater amount of time, the more damage is done to the battery.
Recommended discharge is 0-20%.
For example, in a 100AH battery, only use up 20AH before recharging. Recharge it ASAP.

## Slide 15: Inverter
An inverter steps up the voltage from your battery bank to 220-240v.
Effectively allows you to use it for common household devices.
Inverters come with a rated voltage and two watt values, a continual watt rating and a peak watt rating.
Do not exceed the continual watt rating.
Should be earthed.

## Slide 16: Wiring
What goes where?
The terminals from the solar panels go into the inputs in the charge controller.
The outputs from the charge controller go to the battery bank.
The batteries in the bank are wired together appropriately.
The inverter inputs are wired to the battery bank.
The output of the inverter goes to whichever appliances you’re trying to run.

## Slide 17: Wiring (Cont)
Cable thickness matters!
Thickness is measured in mm2.
Higher currents require thicker cables.
Cables which are too thin will heat up and waste energy. If cables get too hot, they can become a fire hazard.

## Slide 18: Wiring (Cont)
Voltages & amperages matter when wiring up.
With a PWM charge controller, all components must be the same system voltage. The charge controller and all wiring should be rated to handle MORE current than the system can supply.
With MPPT, voltages can be different. To save money on cabling, the panels may be wired up to a higher voltage than the battery bank. Each part of the system needs to be assessed independently and a judgement made on a safe wiring thickness. The wire must be rated to handle the current.

## Slide 19: Fuses & Safety
Everything should be fused.
Fuses can save catastrophe in the event of a mistake or accident.
Earthing must be used. Inverters should be linked to earth so that anything plugged in has an earth connection for safety.
MCBs cut off when too high current. These are useful for protecting devices and limiting unsafe amperages.
RCD detects fluctuations in the current. This is important for high voltages.

## Slide 20: Efficiency
Inefficiencies at every stage:
Charge controller
Batteries
Inverter
You have to cater for all losses. As a rough guide, cater for 30% loss.
Example; 100w comes in, charge controller loses 10w, 90w remaining, batteries lose 9w so 81w remaining, inverter loses 8w and 73w remains.

## Slide 21: Calculating Needs
All devices should have markings which state energy consumption. Watts is required.
The watt rating is the maximum amount of watts used in one hour of continuous use.
If you add up the total number of watt/hours, you can find out roughly how much solar power you’ll need to generate.

## Slide 22: Calculating Needs (Cont)
Example:
PC – 150w – for 4hrs a day = 600wh.
Lights – 20w – for 4hrs a day = 80wh.
Phone Charger – 5w – for 8hrs a day = 40wh.
Add them all together = 720wh.
Cater for loss... Multiply by 1.5 = 1080wh.
Assume 2hrs of good sunlight a day. 1080wh / 2 = 540w. Therefore, 540w of rated panels should suffice. Panels are not usually sold at that high a wattage. Dividing by three gives a figure of 180w. So three 180w panels would do the job.

## Slide 23: Thank you!
Thank you for watching my video...